### TO BE ADDED TO THE GENERAL NOTES

FOR ALL

STORM DRAIN IMPROVEMENT PLANS

- Where utilities need to be supported, said supports shall be in accordance with A.P.W.A. Standard 224-1 unless otherwise indicated.

- Prior to starting construction, the Contractor shall verify location and elevation of existing sewer main(s) and notify the design Engineer of any variation from design.

- The pipe shown hereon shall be installed in accordance with case III bedding as shown on L.A.C.D.P.W. Standard 3080-2, unless otherwise shown.  “W” value shall be as specified on L.A.C.D.P.W. Standard 3080-2 for case III bedding, Notes 3 (a), 3 (b), and 3 (c). If the “W” value at the top of the pipe is exceeded, the bedding shall be modified and/or pipe of additional strength shall be provided. All proposed modifications to this requirement shall be approved by the City Engineer.

- Minimum cover of storm drain main shall be 7 feet from the finished surface per standard drawing 1302-1304.

- Storm drain main stationing is per pipe centerline.

- Street centerline stationing is per the street improvement plans and provided for reference.

- Contractor shall not backfill trench until the City Inspector has obtained as-built stationing on all structures.

- Upon completion of construction of all storm drain lines and prior to paving, the developer shall hire a City approved video company to video tape the pipelines.  City shall review said videotapes for potential construction defects prior to acceptance of the project.